SECTION 26 5313

PHOTOLUMINESCENT EXIT SIGNS

This section includes editing notes to assist the user in editing the section to suit project requirements. These notes are included as hidden text, and can be revealed or hidden by one of the following methods:

Microsoft Word 2007: Click the OFFICE button, select WORD OPTIONS, select DISPLAY, then select or deselect the HIDDEN TEXT option.

Microsoft Word (earlier versions): From the pull-down menus select TOOLS, then OPTIONS. Under the tab labeled VIEW, select or deselect the HIDDEN TEXT option.

Corel WordPerfect: From the pull-down menus select VIEW, then select or deselect the HIDDEN TEXT option.

This master specification section has been prepared by American PERMALIGHT Inc. for use in the preparation of a project specification section covering PERMALIGHT photoluminescent exit signs.

American PERMALIGHT Inc. also offers Section 10 1443 - Photoluminescent Egress Path Markings for specifying photoluminescent directional markings.

The following should be noted in using this specification:

Hypertext links to specific websites are included after manufacturer names and names of organizations whose standards are referenced within the text, to assist in product selection and further research. Hypertext links are contained in parenthesis and shown in blue, e.g.:

(www.astm.com)

Optional text requiring a selection by the user is enclosed within brackets, e.g.: "Section [09 0000.] [_____.]"

Items requiring user input are enclosed within brackets, e.g.: "Section [_____ - ________]."

Optional paragraphs are separated by an "OR" statement, e.g.:

**** OR ****

For assistance on the use of the products in this section, contact American PERMALIGHT Inc. by calling toll-free 888-737-6254, by emailing info@americanpermalight.com or by visiting their website at http://www.americanpermalight.com

PART  	GENERAL

  - SUMMARY

    - Section Includes:

      - Photoluminescent exit signs.

Coordinate the following paragraphs with other sections in the project manual.

    - Related Sections:

      - Division 01: Administrative, procedural, and temporary work requirements.

      - Section 05 5516 – Photoluminescent Metal Stair Nosing

      - Section 10 4500 – Photoluminescent Exit Specialties

      - Section [__ ____ - _______]: Lighting fixtures.

  - REFERENCES

    - Intertek (www.intertek.com) - Directory of Listed Products.

    - National Fire Protection Association (NFPA) (www.nfpa.org) 101 - Life Safety Code.

    - Underwriters Laboratories, Inc. (UL) (www.ul.com):

      - Product Directories.

      - 924 - Standard for the Safety of Emergency Lighting and Power Equipment.

    - Underwriters Laboratories of Canada (ULC) (www.ul.com/canada):

      - CAN/ULC-ORD-C924 - Standard for Photoluminescent and Self-Luminous Exit Signs.

      - CAN/ULC S572 - Photo-Luminescent and Self Luminous Exit Signs and Path Marking Systems.

  - QUALITY ASSURANCE

Edit the following to suit project requirements.

    - Provide exit signs in accordance with [NFPA 101.] [Building Code.]

  - SUBMITTALS

Limiting submittals to only those actually required helps to minimize liability arising from the review of submittals. Minimize submittals on smaller, less complex projects.

Include the following for submission of shop drawings, product data, and samples for the Architect's review.

    - Submittals for Review:

      - Shop Drawings: Indicate exit sign locations, mounting heights, and attachments.

      - Product Data: Include product description, materials, finishes, and performance characteristics.

      - Samples: One full size exit sign. [Sample will be returned for installation on project.]

  - DELIVERY, STORAGE AND HANDLING

    - Store exit signs in protected, dry location until installation.

PART  	PRODUCTS

  - MANUFACTURERS

    - Contract Documents are based on products by American PERMALIGHT Inc.

( www.americanpermalight.com )

Edit the following to indicate whether or not substitutions will be permitted for the products in this section.

    - Substitutions: [Under provisions of Division 01.] [Not permitted.]

  - MANUFACTURED UNITS

    - General Sign Requirements:

      - Self-illuminating, not requiring external power supply, absorbing and storing energy from ambient [LED] [fluorescent] [mercury vapor] [metal halide] light.

      - Non-toxic, non-radioactive. Not self-luminous.

      - High-visibility illumination, energy efficient.

      - Viewing distance: [50] [100] feet.

      - Activation: Minimum 5 fc = 54 lux of [LED] [fluorescent] [mercury vapor] [metal halide] lighting.

Include the following for unframed rigid PVC exit signs; edit to suit project requirements.

    - PVC Photoluminescent Exit Signs - unframed:

      - Sign material: Rigid PVC.

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type: Unframed, with four mounting holes.

      - Letter height: 6 inches.

      - Letter color: [Red.] [Green.]

      - Content: “EXIT”.

      - Sign dimensions: 7-11/16 inches high x 13 inches wide.

      - Directional indicators: Self-adhering chevrons, shipped loose in each package for field installation.

      - Viewing Distance: 50 feet

In the following paragraph signs are furnished with four mounting holes as standard; L-shaped mounting clips are available at additional cost. Double-sided signs require L-shaped mounting clips.

      - Accessories: One Set of two L-shaped mounting clips.

      - Tested to UL 924 by Underwriters Laboratories, Inc.; EXIT signs bear UL Listing Mark, listed in UL Product Directory.

Include the following for framed rigid PVC exit signs; edit to suit project requirements.

    - PVC Photoluminescent Exit Signs – in Frame:

      - Sign material: Rigid PVC.

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type: [Framed in brushed aluminum, silver-anodized color.] [Framed in black aluminum color.]

      - Letter height: 6 inches.

      - Letter color: [Red.] [Green.]

      - Content: “EXIT”.

      - Sign dimensions: 9 inches high x 14-5/8 inches wide.

      - Directional indicators: Self-adhering chevrons, shipped loose in each package for field installation.

      - Viewing Distance: 50 feet

In the following paragraph flat wall-mount accessories are furnished standard; other brackets are available at additional cost. Double-sided signs require mounting brackets.

      - Accessories:

        - Flat wall-mount accessories included in sign package.

        - [1.5 inch bracket for ceiling or perpendicular mount.]

        - [10 inch extended ceiling mount bracket.]

        - [19.5 inch extended ceiling mount bracket.]

      - Tested to UL 924 by Underwriters Laboratories, Inc.; EXIT signs bear UL Listing Mark, listed in UL Product Directory.

Include the following for unframed aluminum exit signs; edit to suit project requirements.

    - Aluminum Photoluminescent Exit Signs - unframed:

      - Sign material: Aluminum.

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type: Unframed, with four mounting holes.

      - Photoluminescent Letter height: 7 inches.

      - Aluminum Background color: [Red.] [Green.]

      - Content: “EXIT” and directional indicators imprinted.

      - Sign dimensions: 8-1/2 inches high x 17 inches wide.

      - Directional indicators: permanently imprinted on Aluminum surface. Must determine in beforehand if sign shall read EXIT, <EXIT, EXIT> or <EXIT>.

      - Viewing Distance: 50 feet

In the following paragraph signs are furnished with four mounting holes as standard; L-shaped mounting clips are available at additional cost. Double-sided signs require L-shaped mounting clips.

      - Accessories: One Set of two L-shaped mounting clips.

      - Tested to UL924 by Intertek; EXIT signs bear ETL Listed Mark, listed in Intertek Directory of Listed Products.

      - Tested to CAN/ULC-ORD-C924 by Intertek; bear cETL Listed Mark, listed in Intertek Directory of Listed Products.

Include the following for framed aluminum exit signs; edit to suit project requirements.

    - Aluminum Photoluminescent Exit Signs – in Frame:

      - Sign material: Aluminum.

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type:  Framed in aluminum, color-matched to Aluminum background color.

      - Photoluminescent Letter height: 7 inches.

      - Aluminum Background color: [Red.] [Green.] [Black.]

      - Content: “EXIT”.

      - Sign dimensions: 10-1/4 inches high x 18-3/4 inches wide.

      - Directional indicators: Chevrons shipped loose in each sign package, for field installation.

      - Viewing Distance: 50 feet

In the following paragraph flat wall-mount accessories are furnished standard; other brackets are available at additional cost. Double-sided signs require mounting brackets.

      - Accessories:

        - Flat wall-mount accessories included in sign package.

        - [1.5 inch bracket for ceiling or perpendicular mount.]

        - [10 inch extended ceiling mount bracket.]

        - [19.5 inch extended ceiling mount bracket.]

      - Tested to UL 924 by Intertek; EXIT Signs bear ETL Listed Mark, listed in Intertek Directory of Listed Products.

      - Tested to CAN/ULC-ORD-C924 by Intertek; bear cETL Listed Mark, listed in Intertek Directory of Listed Products.

Include the following for acrylic exit signs; edit to suit project requirements.

    - Acrylic Photoluminescent Exit Signs:

      - Sign material: Acrylic.

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type: Unframed, with four mounting holes.

      - Photoluminescent Letter height: 7 inches.

      - Acrylic Background color: [Red.] [Green.] [Black.]

      - Content: “EXIT” and directional indicators sub-surface printed.

      - Sign dimensions: 8-3/4 inches high x 17-1/4 inches wide.

      - Directional indicators: permanently sub-surface imprinted. Must determine in beforehand if sign shall read EXIT, <EXIT, EXIT> or <EXIT>.

      - Viewing distance: 50 feet

In the following paragraph stand-off barrel sets and wire suspension sets are available at additional cost.

      - Accessories:

[Stand-off barrel set for projected installation.]

[24 inch wire suspension set.]

Tested to UL 924 by Intertek; EXIT signs bear ETL Listed Mark, listed in Intertek Directory of Listed Products.

Tested to CAN/ULC-ORD-C924 by Intertek; bear cETL Listed Mark, listed in Intertek Directory of Listed Products.

Include the following for Outdoor- and Wet Location tested exit signs with UL924-listed 100-foot Viewing Distance; edit to suit project requirements.

    - Outdoor / Wet Location suited / 100-foot Viewing Distance Photoluminescent Exit Signs:

      - Sign material: ABS plastic panel

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type:  unframed.

      - Photoluminescent Letter height: 6 inches.

      - ABS plastic background color: [Red.] [Green.] [Black.]

      - Content: “EXIT”.

      - Sign dimensions: 8-5/8 inches high x 15-7/8 inches wide.

      - Directional indicators: Chevrons shipped loose in each sign package, for field installation.

      - Viewing Distance: 100 feet

In the following paragraph one Mounting Bracket is furnished standard. Double-sided signs require mounting bracket.

      - Accessories:

a. Mounting Bracket included in sign package. Designed for flag, ceiling and conduit mounting.

11.     Tested to UL 924 by Underwriters Laboratories, Inc.; EXIT Signs bear UL Listing Mark, listed in UL Product Directory.

Include the following for UL924-listed for LED (Light Emitting Diode) activation 100-foot Viewing Distance exit signs; edit to suit project requirements.

    - LED Activation 100-foot Viewing Distance Photoluminescent Exit Signs:

      - Sign material: plastic housing.

      - Sign type: [[Single] [Double] sided.] [As scheduled at end of Section.]

      - Frame type:  unframed.

      - Photoluminescent Letter height: 6 inches.

      - Housing color: [Red.] [Green.]

      - Content: “EXIT”.

      - Sign dimensions: 8.75 inches high x 15.5 inches wide.

      - Directional indicators: Chevrons integrated into housing. If needed on-site, chevrons get punched out of housing during field installation.

      - Viewing Distance: 100 feet

In the following paragraph one Mounting Bracket is furnished standard. Double-sided signs require mounting bracket.

      - Accessories:

        - Mounting Bracket included in sign package. Designed for flag, ceiling and conduit mounting.

      - Tested to UL 924 by Underwriters Laboratories, Inc.; EXIT Signs bear UL Listing Mark, listed in UL Product Directory.

  - ACCESSORIES

    - Fasteners: Type best suited to application.

PART  	EXECUTION

  - INSTALLATION

Install signs in accordance with manufacturer’s instructions and approved Shop Drawings.

Edit the following to suit project requirements.

Locate signs to conform to [Building Code.] [NFPA 101.]

Install directional indicators to suit project requirements.

Set signs plumb, level, and rigid.

Attach signs to supporting construction.

SCHEDULE

Consider including a schedule listing the products in this section. Coordinate with Part 2 - Products and with drawing designations.

| SIGN DESIGNATION | SIGN MATERIAL | SIGN TYPE | MOUNTING TYPE |
| --- | --- | --- | --- |
| ES-1 | PVC | Double sided, framed | Ceiling, with 10 inch extension bracket |
| ES-2 | Aluminum | Single sided, unframed | Perpendicular to wall, with two L-shaped mounting clips |
| ES-3 | Aluminum | Single sided, framed | Flat on wall, using accessories from sign package |
| ES-4 | Acrylic | Single sided, left directional indicator | Flat on wall, with four stand-off barrels |
| ES-5 | ABS panel 100-foot | Single sided, left and right directional indicators | In Outdoor – and Wet Location environments, such as Swimming Pool areas: Ceiling mount with mounting bracket |
| ES-6 | LED activation 100-foot viewing distance | Single sided, right directional indicator | Perpendicular to wall, using mounting bracket from sign package |

END OF SECTION